光伏系统用铜芯无卤电缆

Copper core halogen-free cable for Photovoltaic system

产品型号Product name:  TUV PV1-F

产品认证 Approvals: TUV Rheinland 2PfG 1169 1.5mm2-35mm2 (Multiple color)

产品结构Cable structure:

常用参数 Common Parameters:

| 导体截面 Cross Section (mm2) | 导体结构 Conductor Construction (n/mm) | 导体绞合外径 Conductor Stranded OD. （mm） | 成品近似外径 Cable appr. OD. (mm) | 导体直流电阻 Conductor Max. Resistance @20℃（Ω/km） | 载流量 Current Carrying Capacity @60℃（A） |
| --- | --- | --- | --- | --- | --- |
| 1.5 | 30/0.25 | 1.58 | 4.90 | 13.7 | 30 |
| 2.5 | 49/0.25 | 2.02 | 5.45 | 8.21 | 41 |
| 4 | 56/0.285 | 2.50 | 5.60 | 5.09 | 55 |
| 6 | 84/0.285 | 3.17 | 5.90 | 3.39 | 70 |
| 10 | 84/0.40 | 4.56 | 9.00 | 1.95 | 98 |
| 16 | 126/0.40 | 5.60 | 10.20 | 1.24 | 132 |
| 25 | 192/0.40 | 6.95 | 12.00 | 0.795 | 176 |
| 35 | 276/0.40 | 8.74 | 13.80 | 0.565 | 218 |

*此载流量为电缆单根敷设于空气中的情况

The current-carrying capacity is under the situation of laying the single cable in air.

技术参数 Technical Data:

额定电压Nominal voltage：0.6/1.0KV AC, 1.8KV DC

成品电压测试 Voltage test on completed cable: 6.5KV AC, 15KV DC, 5min

环境温度Ambient temperature: -40℃~+90℃

导体最高温度Max. Temperature of conductor: +120℃

使用寿命Service life: ≥25 years (Ambient temperature: -40℃~+90℃)

参考短路允许温度Short circuit allowed temperature refer to: 200℃ in 5 seconds

弯曲半径Bending radius: ≥4×φ (D<8mm), ≥6×φ (D≥8mm)

耐酸碱测试Acid & Alkaline resistance: EN60811-2-1

冷弯测试Cold bending test: EN60811-1-4

耐候/紫外线测试Weathering/UV resistance: HD605/A1

耐臭氧测试O-zone resistance: EN50396

耐穿透性Penetration resistance: Accord with 2PfG 1169/08.2007

无卤阻燃测试Halogen-free flame retardant test: Refer to 2PfG 1169/08.2007, EN50618, IEC60332-1, IEC61034, UL1581 VW-1, etc