光伏系统用铜芯无卤电缆

Copper core halogen-free cable for Photovoltaic system

产品型号Product name:  UL PV

产品认证 Approvals: UL4703 PV 18AWG-2AWG

产品结构Cable structure:

常用参数 Common Parameters:

| 导体截面 Cross Section (AWG) | 导体结构 Conductor Construction (n/mm) | 导体绞合外径 Conductor Stranded OD. （mm） | 600V 成品外径 Cable OD. (mm) | 1KV/2KV成品外径Cable OD. (mm) | 导体直流电阻 Conductor Max. Resistance @20℃（Ω/km） | 载流量 Current Carrying Capacity @60℃（A） |
| --- | --- | --- | --- | --- | --- | --- |
| 18 | 16/0.254 | 1.18 | 4.25 | 5.00 | 23.20 | 6 |
| 16 | 26/0.254 | 1.49 | 4.55 | 5.30 | 14.60 | 6 |
| 14 | 41/0.254 | 1.88 | 4.95 | 5.90 | 8.96 | 6 |
| 12 | 48/0.30 | 2.36 | 5.40 | 6.20 | 5.64 | 6 |
| 10 | 105/0.254 | 3.00 | 6.20 | 7.05 | 3.546 | 7.5 |
| 8 | 168/0.254 | 4.10 | 7.90 | 8.70 | 2.23 | 7.5 |
| 6 | 266/0.254 | 5.20 | 9.80 | 10.30 | 1.403 | 7.5 |
| 4 | 420/0.254 | 6.50 | 11.50 | 11.60 | 0.882 | 7.5 |
| 2 | 665/0.254 | 8.25 | 13.30 | 13.40 | 0.5548 | 7.5 |

*此载流量为电缆单根敷设于空气中的情况

The current-carrying capacity is under the situation of laying the single cable in air.

技术参数 Technical Data:

额定电压Nominal voltage：600V, 1000/2000V AC

成品电压测试 Voltage test on completed cable:

U=600V: 18~10AWG, U0=3000V, 50HZ, 1Min；8~2AWG, U0=3500V, 50HZ, 1Min.

U=1000/2000V: 18~10AWG, U0=6000V, 50HZ, 1Min；8~2AWG, U0=7500V, 50HZ, 1Min.

环境温度Ambient temperature: -40℃~+90℃

导体最高温度Max. Temperature of conductor: +120℃

相对介电常数Relative permittivity: UL854

冷弯测试Cold bending test: UL854

耐日光测试Sunlight resistance: UL2556

阻燃测试Flame retardant test: UL1581 VW-1